An Advanced Computer Code for Single-Tuned Harmonic Filter Design

KUN-PING LIN

NATIONAL TAIWAN UNIVERSITY

Tainan, Taiwan R.O.C.

Abstract ___ The objective of this paper is to present a novel approach for limiting harmonic and improving reactive compensation for industrial power systems using single-tuned filters. The unique feature of the developed power distribution model is that it incorporates both the filter’s capacity and resonant point as design parameters. The model also considers the de-tuning effects due to temperature and frequency variations, as well as manufacturing tolerances.  The proposed approach was implemented as a PC-based computer code, and it was integrated with a user-friendly graphical user interface.  The developed analysis tool was employed to solve the harmonic problems of several industrial plants, and the results all showed great improvements after using this computer tool.

I.	INTRODUCTION

The IEEE filter design practices for limiting harmonic and improving reactive compensation is depicted in Fig. 1 [1].  It requires that the capacitor’s voltage and capacity, and the reactor impedance have to be pre-determined.  For engineers not knowing the appropriate initial estimates, the process has to be repeated until all the proper values are found.  This trial-and-error approach can become very complex as more filters are included in the systems.

NO

NO

YES

YES

NO

IS

FILTER OUTPUT

KVAR ENOUGH

SELECT CAPACITOR

KV & KVAR RATINGS

DETERMINE REACTOR

IMPEDANCE

INCREASE

KV RATING

IS

THD BELOW

MAXIMUM LIMIT?

IS

CURRENT RATING

APPROPRIATE?

IS

VOLTAGE RATING

APPROPRIATE?

FILTER DESIGN

COMPLETED

RECONSIDER DESIGN

AND START AGAIN

IS

NEW RESONANCE

THE CAUSE?

INCREASE

KVAR RATING

NO

YES

YES

YES

Fig. 1.  Decision flowchart for single-tuned filter design.

This paper presents a new approach that incorporates a novel power distribution model.  The proposed distribution model eliminates the trial-and-error approach by including both the filter’s capacity and the resonant point as design parameters. The model also considers the de-tuning effects due to temperature and frequency variations, as well as manufacturing tolerances.

Computer programs have become useful design tools for electrical engineers in recent years as in harmonic analysis and filter design [1,2].  The proposed approach was implemented as a PC-based computer code.  A user-friendly graphical user interface (GUI) was also integrated as a module to the developed computer code.  The simulation process is fully automated, and the numerical turnaround is very fast.  The analysis tool enables the detailed examination of each individual as well as the total harmonic distortions at the point of common coupling (PCC).  The program also recommends filter with specifications appropriate to the system.

This paper first presents the proposed new approach with the mathematical formulations of the novel power distribution model.  The model implementation and solution procedure are then introduced.  An industrial plant with existing harmonic problems was selected to demonstrate the capabilities of the developed analysis tool for limiting harmonics and improving reactive compensation using single-tuned filters.

II. TECHNICAL APPROACH

The new approach proposed here involves seven steps as depicted in Fig. 2.  Step 1 is to perform the analysis and identify those unwanted harmonic distortions in the system.  Based on the review, the necessary filters are included in the system.  It is noted that the filter limiting the lowest order harmonic distortion should be installed first, so the parallel resonance can be avoided.

Steps 3 and 4 are the core of the current approach.  It is essentially a power distribution model that incorporates both the reactive power Qfhand resonant pointnhas design parameters.  First, the power system has to be formulated to take those added filters into accounts.  To avoid any possible series resonance, the added filters have to be designed to function regardless of the variation of power sources and manufacturing tolerances.  This means the derived system formulations are  subject to certain design constraints, so the filter de-tuning from its design value can not devastate the entire system.  To solve the system formulations with constraints, the so called Sequential Unconstrained Minimization Technique [3] was employed.  The solutions Qfhand nh are then obtained for each filter added in the system.

START

SYSTEM ANALYSIS

BEFORE FILTERS INSTALLED

INCLUSION OF THE NECESSARY

FILTERS IN THE SYSTEM

SYSTEM FORMULATIONS

& CONSTRAINTS

SOLVING  FOR reactive power QFh

AND resonant point, nh, for each  h--th filter

USING  the s.u.M.T.

ARE

ALL THE REQUIREMENTS

MET?

NO

RECOMMENDATION OF FILTERS

WITH PROPER SPECIFICATION

BASED ON RESULTS OF SIMULATION

END

STEP 1

STEP 2

STEP 3

STEP 4

STEP 5

STEP 6

SYSTEM ANALYSIS

AFTER  
 AND 
FOUND

STEP 7

YES

Fig.  2.  Flowchart of the proposed approach.

Step 5 is to perform system analysis after the designed Qfhand nh are found.  Based on the results from Step 5, Step 6 checks the system for existence of any unwanted harmonic distortion and parallel resonance resulting from the filters added.  If any requirement is not met, the process is started over beginning from Step 2.  If all the requirements are satisfied, the appropriate filter component ratings are then determined.

It is noted here that the approach outlined in Fig. 2 was implemented as a PC-based computer program, and the procedure is fully automated.  No trial and error is needed.

III. SYSTEM FORMULATIONS AND CONSTRAINTS

This section presents the mathematical formulations of the power distribution model as Step 3 in Fig. 2.  The formulations are first derived based on a simple example, and then generalized for more complex systems.  The filter design constraints to the system equations are also described.

A. System Equations

Fig. 3 shows a typical one-line diagram of an industrial plant that contains two harmonic loads A and B, and two AC loads M1 and M2.  To focus on the power distribution model, we skip Steps 1 and 2 by assuming the 5-th, 7-th, 11-th, and 13-th order harmonic distortions have be improved. And, we decide to add four single-tuned filters, and analyze the system at 60 Hz.

The impedance, PU, of the electric source, the transformer, the two AC loads, and the four added filters are expressed in the following:

XS=1S	, where S=SCCSb												(1)

Xt=1St	, where St=100T´STSb								(2)

XM1=1SM1	where SM1=100M1´SL1Sb								(3)

XM2=1SM2	where SM2=100M2´SL2Sb							(4)

XC5=1SF5	where SF5=QF5Sb´1−1n52						(5)

XC7=1SF7	where SF7=QF7Sb´1−1n72						(6)

XC11=1SF11	where SF11=QF11Sb´1−1n112						(7)

XC13=1SF13	where SF13=QF13Sb´1−1n132						(8)

where

SCC		source short circuit capacity;

Sb			base capacity;

QFh		filter capacity h=5,7,11, and 13;

nFh		filter resonant point h=5,7,11, and 13.

The two harmonic loads A and B can be represented by a single harmonic current source Ih.  Fig. 4 depicts the equivalent circuit of the power system at 60 Hz. It is noted that the inductive impedance of the four filters is expressed as (Xch /nh2) where h=5,7,11, and 13, so the added filters can limit their corresponding h-th harmonic distortion.

VCB

500uf x3

500uf x3

500uf x3

A

11.4 KV

PCC

Sb=1000 KVA

Vb=11.4 KV

Sb=1000 KVA

Vb=380 V

11.4KV/220V, 380,440

T%  ST KVA

380V-BUS

CIB

S1 KVA

PF1

S2 KVA

PF2

M2%

SL2 HP

PF4

B

M1%

SL1 HP

PF4

M

M

M

M

Fig. 3.  A typical one-line diagram of an industrial plant.

Ih

j1S

j1St

1/(SM1+SM2)

j(Xc5/n52)-jXc5

QF5

j(Xc7/n72)-jXc7

QF7

j(Xc11/n112)-jXc11

QF11

j(Xc13/n132)-jXc13

QF13

Fig. 4.  The resultant equivalent circuit at 60 Hz.

However, it is important to understand that the resonant point nh must not be equal to the order h of the harmonic distortion (i.e., nh¹h). This is to avoid the filters being burned out due to series resonance.  For example, the design resonant point nh of the filter responsible for limiting 5-th harmonic distortion should be a real number near the integer 5, but not the exact integer 5.  Therefore, when limit the h-th order harmonic distortion, the equivalent circuit shown in Fig. 4 is rearranged by multiplying the inductive impedance by a factor h, and by dividing the capacitance by a factor h.  Fig. 5 shows the resultant equivalent circuit that is valid for any h-th order harmonic distortion. Two observations from Fig. 5 are stated in the following:

- When QFh is fixed, the filter impedance Z increases as nh decreases.

- When nh is fixed, the filter impedance Z increases as QFh decreases.

jhSM1+SM2

jSbQF7h2−n72hn72−1

jSbQF5h2−n52hn52−1

Ithh

QF7

QF13

QF5

jSbQF13h2−n132hn132−1

IMh

IF5h

IF7h

IF11h

IF13h

j(h/st)

j(h/s)

Ish

QF11

Fig. 5.  The resultant equivalent circuit for any h-th order harmonic distortion where h=1,N.

The harmonic distortion Dh at the point of common coupling (PCC) should meet the IEEE-519 Standards.  Assuming the bus voltage is VBUS, we derive the expression for the harmonic distortion in the following.

ISh=VBUSZSh+Zth(PU)														(9)

IMh=VBUSZMh(PU)																(10)

IFih=VBUSZFih(PU)	, i=5, 7, 11, and 13, and h=2, 3,.., 50	(11)

where

ZSh = jhS, Zth = jhSt, and ZMh = jhSM1+SM2

We also know,

Ithh=ISh+IMh+IF5h+IF7h+IF11h+IF13h							(12)

where Ithh is the h-th harmonic current from the harmonic current source in the model ckt. Ihis the actual harmonic current obtained from the manufacture.  Therefore, the actual harmonic current at the PCC has to be scaled based on the following equation:

ISh'=ISh´(IhIthh)																(13)

The h-th harmonic distortion can then be expressed by the following equation:

Dh=ISh'IL1´100%																(14)

where IL1 is the PU value of the rated current at PCC.  Equation (14) can be simplified by neglecting the IMh without loss of generality, and by employing (1)-(13), which gives the following expression for Dh:

Dh=(IhIL1)(Xsh+Xth)(1Xsh+Xth)+(h2Sb)[−DQc+(h2−1)(QF5h2−n52+QF7h2−n72+QF11h2−n112+QF13h2−n132)]																							(15)

Equation (15) can further be expressed in a more generalized form that is valid for any number of filters by the following equation:

Dh=(1XSh+Xth)(IhIL1)(1XSh+Xth)+(h2Sb)[−DQc+(h2−1)i=m1mfQFih2−ni2]			(16)

The total harmonic distortion THDi can then be expressed in terms of the individual harmonic distortion of Dh as follows:

THDi=h=250Dh2																(17)

The objective here is to minimize the THDi which is subject to the constraints discussed in the following section.

B. System Constraints

The system equations derived above are subject to several constraints such as:

- reactive compensation;

- IEEE standards for maximum harmonic distortions;

- power source variations; and

- filter de-tuning.

These factors serve as the boundary conditions of the system equations.  The power system in Fig. 3 is used as an example to demonstrate how these constraints are evaluated in the computer program.

1) Reactive Compensation: The summation of the filter’s reactive power has to be equal to the reactive power compensation as expressed in the following:

QF5+QF7+QF11+QF13=DQc										(18)

2)	IEEE Standards for Maximum Harmonic Current Distortion: The harmonic distortion Dh has to meet the IEEE-519 standards [4] contained in the following table:

TABLE I

IEEE-519 Standards for Maximum Harmonic Current DISTORTIONS.

| MAXIMUM HARMONIC CURRENT DISTORTION (%) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | HARMONIC ORDER (ODD HARMONICS) |  |  |  |  |  |
| ISC/IL | h<11 | 11h<17 | 17h<23 | 23h<35 | h ³35 | THDi % |
| <20 | 4.0 | 2.0 | 1.5 | 0.0 | 0.3 | 5.0 |
| 20-50 | 7.0 | 3.5 | 2.5 | 1.0 | 0.5 | 8.0 |
| 50-100 | 10.0 | 4.5 | 4.0 | 1.5 | 0.7 | 12.0 |
| 100-1000 | 12.0 | 5.5 | 5.0 | 2.0 | 1.0 | 15.0 |
| >1000 | 15.0 | 7.0 | 6.0 | 2.5 | 1.4 | 20.0 |

If ISC/IL < 20, Table I gives the upper bound of the 5th, 7th, 11th, and 13th harmonic current distortions in the following:

0<D5<4% 																	(19)

0<D7<4% 																	(20)

0<D11<2% 																	(21)

0<D13<2% 																	(22)

3) System Variations: The power supplied by the Taiwan Electric Power Company has a ±5%variation in voltage approximately.  This means the SCC value does not remain constant, but rather varies between the lower and upper limits SCCmin and SCCmax, respectively.  Another uncertainty is the frequency of the power supply contains ±1% variation as expressed in the following:

Dff≤1%																			(23)

4)	Filter De-tuning: Filter de-tuning can result in the series resonance between the designed resonant point nh and the h-th harmonic.  There are two major factors that contribute to the filter de-tuning, namely, temperature variation and manufacturing tolerance.  The capacitance, for example, can have ±2% variations from its designed value due to season changes (i.e., summer vs. winter).  It can also have -5%~+10% variations due to the manufacturing.  Therefore, the resultant variation in capacitance is define by the following equation:

−7%≤DCC≤12%															(24)

Since most of the reactors use air core, its inductance is not affected by temperature variations, but still subject to variation due to manufacturing tolerances.  In general, there is an approximate±3% variation from its designed value, which is expressed in the following:

−3%≤DLL≤3%																(25)

5) Safe Design Range for Resonant Point: The designed resonant point for a single tune filter is determined by the following equation [5]:

nh=12p⋅fLC																(26)

Equation (26) states that the designed resonant point, nh, is a function of frequency, and filter’s inductance and capacitance.  Any variation of these parameters can deviate the resonant point from its originally designed value.  The resultant possible deviation from the designed value can be obtained by substituting (23)-(25) in (26) as in the following:

h´11.01´1.03´1.12<nh<h´10.99´0.97´0.93   or,

0.92h nh 1.06h																(27)

For example, if h=5, (14) gives 4.60≤n5≤5.30, and if h=4.6, (14) gives 4.23≤n4.6≤4.88.  This means that to design a filter suppressing the 5-th order harmonic, and to preventing the filter from possible series resonance,  the proper design range is 4.6 or less.  Fig. 6 depicts the idea of determining the safe range for the designed resonant point.  For any h-th harmonic, the safe range for determining resonant point is defined in the following:

(h−1)<nh≤0.92´h														(28)

where nh is the designed resonant point, and h is the order of the harmonic to be suppressed by the designated filter. 	Based on the above discussion, the safe design ranges of the resonant points for the four designated filters for suppressing the 5-th, 7-th, 11-th, and 13-th filters are summarized in the following:

4<n5≤5´0.92																(29)

6<n7≤7´0.92																(30)

10<n11≤11´0.92															(31)

12<n13≤13´0.92															(32)

IV.	MODEL IMPLEMENTATION

In Section III, we presented the mathematical formulations of the proposed power distribution model.  This section explains the procedure and technique employed for obtaining the solutions.  The program was written in the Visual Basic, and implemented on a PC based computer.

A.  Governing Equations

The system formulations and their constraints can be generalized for obtaining the solutions, namely, Qfm[i] and nm[i] by minimizing the THDi, which are described by the following expression:

minTHDi=minf(QFm[i],nm[i])=minh=250Dh2			(33)

ORDER OF HARMONIC

4

4.23

4.87

4.6

Safe

Design Range

6

5

Fig. 6. Determination of safe range for designed resonant point.

subject to the following constraints:

i=1pQFm[i]=DQcwhere QFm[i]>0, i=1,2,.., p and p50		(34)

0<Dm[j]<Mcr%, j=1,2,..., 50										(35)

m[i]−1<nm[i]≤m[i]´92%												(36)

where

m[i]	order of the harmonic to be suppressed;

nm[i]	designed resonant point of the filter suppressing the harmonic of order m[i];

Dm[j]	harmonic current distortion;

QFm[i]	reactive power of the filter suppressing the m[i]-th order harmonic;

DQc	reactive power compensation;

Mcr		IEEE-519 standards for maximum harmonic distortion c=1,..,5 and r=1,..,5.

B. Solution Procedure

To solve (33), both the Fermat Theorem and the so called SUMT (Sequential Unconstrained Minimization Technique) [6] was employed.

By assuming DQ=10 MVAR, Table II contains the solutions of the system shown in Fig. 3 by using the developed computer program.

TABLE II

SOLUTION QFiand ni

| i-th ORDER HARMONIC | QFi | ni |
| --- | --- | --- |
| 5 | 2.37 | 4.60 |
| 7 | 1.69 | 6.44 |
| 11 | 3.20 | 10.12 |
| 13 | 2.74 | 11.96 |

With known QFi and ni, the capacitance C and the inductance L can be calculated using (5)-(8) and (26).  The harmonic current at each port of the filter limiting i-th order harmonic is calculated by the following equation:

IFih'=IFih´(IhIthh)																(37)

The reactor protective current is calculated using the following equation:

IFi=h=150IFih´130%														(38)

The capacitor protective voltage is calculated using the following equation:

Vci=h=150(IFih'´Xcih)2´110%											(39)

With all these design values calculated by the computer program, filters meeting all these specifications can then be ordered from the suppliers.

V. AN APPLICATION EXAMPLE

In this section, we employ the developed computer program to resolve the harmonic problems of a small industrial plant.  Fig. 7  depicts the one-line diagram of the plant.  The plant has an AC load and a harmonic load, and one of the objective is to improve the power factor from 0.76 to 0.98.  To determine the appropriate filters for the system, we follow the approach outlined in Fig. 2.  First, we analyze the system before any filter is added to it.

A. System Analysis Before Filters Installed

Table III contains the information of the power system shown in Fig. 7. From the above table, we get ISC/IL=73.68.  The ratio determines the maximum allowable harmonic current distortions from Table I.  The plant engineers also provided a list of the harmonic currents in the system.  This information is contained in Table IV.

B. Inclusion of Necessary Filters

From the system analysis before filters being installed, it is obvious that the 5-th, 11-th, 23-th, and 25-th order of harmonic currents are over the maximum allowable limits.  These four harmonic currents are indicated in Table V.  We first include two single-tuned filters for suppressing the 5-th and 7-th order harmonics.

TAIWAN ELECTRICAL

POWER COMPANY

PCC

69KV

SCC=641MVA

AC LOAD

HARMONIC

LOAD

FILTER

REAL POWER=4410KW

AVERAGE POWER FACTOR=0.76

Fig. 7.  One-line diagram of a small industrial plant.

Table III

System Information of the Plant

| PARAMETER | VALUE |
| --- | --- |
| Vs | 69.0 KV |
| Sb | 10.0 MVA |
| SCCmin | 641.0 MVA |
| St | 8705.0 KVA |
| ISC | 5363.7 A |
| IL | 72.8 A |
| PORT AT BUS | 3.3 KV |
| LOAD | 5802 KVA |

Table Iv

HARMONIC CURRENTS Ih  IN THE SYSTEM

| ORDER | CURRENT (A) | ORDER | CURRENT (A) | ORDER | CURRENT (A) | ORDER | CURRENT (A) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 1014.8 | 5 | 173.0 | 7 | 44.0 | 11 | 52.0 |
| 13 | 23.0 | 17 | 29.0 | 19 | 19.0 | 23 | 19.0 |
| 25 | 12.0 | 29 | 9.0 | 31 | 4.8 | 35 | 2.9 |
| 37 | 2.0 | 41 | 1.3 | 43 | 1.3 | 47 | 1.8 |
| 49 | 1.4 |  |  |  |  |  |  |

Based on the information provided in Tables III and IV, the PU transformation was performed and summarized in the following table:

Table V

PU TRANSFORMATIONS

| SOURCE IMPEDANCE (Zs)PU TRANSFORMATION |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| XZs=(1.0´PU)´SbSCCs=(1.0´PU)´(10641)=j0.015601PU |  |  |  |  |  |  |  |  |
| TRANSFORMER IMPEDANCE (Zt) PU TRANSFORMATION |  |  |  |  |  |  |  |  |
| XZt=(0.07´PU)´SbSCCt=(0.07PU)´108.705=j0.080414PU |  |  |  |  |  |  |  |  |
| BASE LOAD CURRENT PU TRANSFORMATION |  |  |  |  |  |  |  |  |
| IL(PU)=IL[10MVA(3´69KV)]=72.8´0.011951PU=0.87PU |  |  |  |  |  |  |  |  |
| HARMONIC CURRENT PU TRANSFORMATION |  |  |  |  |  |  |  |  |
| Ih(PU)=Ih[10MVA(3´3.3KV)]=Ih´0.00057PU |  |  |  |  |  |  |  |  |
| ORDER | CURRENT PU TRANS. | ORDER | CURRENT PU TRANS. | ORDER | CURRENT PU TRANS. | ORDER | CURRENT PU TRANS. |  |
| 1 | 0.5800 | 5 | 0.0989 | 7 | 0.0251 | 11 | 0.0297 |  |
| 13 | 0.0131 | 17 | 0.0166 | 19 | 0.0109 | 23 | 0.0109 |  |
| 25 | 0.0069 | 29 | 0.0051 | 31 | 0.0027 | 35 | 0.0017 |  |
| 37 | 0.0011 | 41 | 0.0007 | 43 | 0.0007 | 47 | 0.0010 |  |
| 49 | 0.0008 |  |  |  |  |  |  |  |

The calculated harmonic current distortions by the computer program are summarized in Table VI as follows.

Table VI

PCC INDIVIDUAL AND tOTAL DISTORTIONS OF HARMONIC CURRENTS

| ORDER | Dh(%) | ORDER | Dh(%) | ORDER | Dh(%) | ORDER | Dh(%) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2 | 0.000 | 3 | 0.000 | 4 | 0.000 | 5 | 11.361 |
| 6 | 0.000 | 7 | 2.883 | 8 | 0.000 | 9 | 0.000 |
| 10 | 0.000 | 11 | 3.412 | 12 | 0.000 | 13 | 1.505 |
| 14 | 0.000 | 15 | 0.000 | 16 | 0.000 | 17 | 1.907 |
| 18 | 0.000 | 19 | 1.252 | 20 | 0.000 | 21 | 0.000 |
| 22 | 0.000 | 23 | 1.252 | 24 | 0.000 | 25 | 0.793 |
| 26 | 0.000 | 27 | 0.000 | 28 | 0.000 | 29 | 0.586 |
| 30 | 0.000 | 31 | 0.310 | 32 | 0.000 | 33 | 0.000 |
| 34 | 0.000 | 35 | 0.195 | 36 | 0.000 | 37 | 0.126 |
| 38 | 0.000 | 39 | 0.000 | 40 | 0.000 | 41 | 0.080 |
| 42 | 0.000 | 43 | 0.080 | 44 | 0.000 | 45 | 0.000 |
| 46 | 0.000 | 47 | 0.115 | 48 | 0.000 | 49 | 0.090 |
| THDi=249Dh2=12.619% |  |  |  |  |  |  |  |

It is noted here that the filter suppressing lower order harmonic should be installed earlier.  This is to avoid the possible parallel resonance between the lower harmonic and the filter designated for suppressing the higher order harmonic.

C. 	System Formulations and  Constraints

The system formulations and constraints are depicted in Fig. 8.

D. Obtaining Solutions Using The S.U.M.T.

The solutions QFi and ni (i=5 and 7) were obtained using the S.U.M.T. implemented in the program.  Table VII contains the results calculated by the program.  It is noted that it took 17.6 seconds in getting the converged solutions.

E. System Analysis After Filters Being Installed

From the solutions QFi and ni (i=5 and 7) obtained above, the distortions of harmonic currents and voltages at PCC can then be evaluated using (16).  Figs. 9 and 10 compare the improvements before and after the two filters being installed.  From the comparison, it is seen that all harmonics were greatly improved after adding the two filters.  It is also noted that no parallel resonance was observed after the two filters were installed in the system.

From the results, it is obvious that the developed power distribution model is very capable of limiting harmonics and improving reactive compensation.  Also, the implemented computer program also shows very quick turnaround in obtaining the solutions.

F. Recommendations of Filters with Proper Specifications

Up to this point, the proper design values of the two added filters are well defined.  The protective current and voltage of the two filters are evaluated from the calculated C and L values contained in Table VII.

To solve for (QF5,n5)and (QF7,n7) by minimizing

THDi:

min(THDi)

subject to:

0<D5<5%;

0<D11<2.25%;

0<D23<0.75%;

0<D25<0.75%;

QF5+QF7=2.875

QF5>0;and

QF7>0.

where

Dh=(10.0156h+0.0804h)´(Ih72.8)(10.0156h+0.0804h)+h210[−2.875+(h2−1)(QF5h2−n52+QF7h2−n72)]

Fig. 8. System equations and constraints.

Table VII

SOLUTIONS COMPUTED BY THE PROGRAM

| FILTER | F(#5) | F(#7) |
| --- | --- | --- |
| ni | 4.60 | 6.44 |
| QFi (KVAR) | 1615 | 1260 |
| C (uf) | 375 | 300 |
| L (mh) | 0.887 | 0.566 |
| Solution Time: 17.6 Seconds |  |  |

THDi=12.618%

THDi=3.045%

Fig. 9. Comparison of harmonic currents before and after the two filters suppressing the 5-th and the 7-th harmonics being installed.

THDv=1.273%

THDv=0.494%

Fig. 10. Comparison of harmonic voltages before and after the two filters suppressing the 5-th and the 7-th harmonics being installed.

TABLE VIII

Recommended Protective Current and Voltage

| FILTERS | F(#5) | F(#7) |
| --- | --- | --- |
| Protective Current (AMP) | 325.9 | 231.5 |
| Protective Voltage (KV) | 3.98 | 3.96 |

G. Situations When More Than Two Filters Added in the System

Although only two filters were needed to satisfy all the system requirements, it is interesting to study the situations when more than two filters are installed in the system.  A simulation was performed to examine the situation when three filters suppressing the 5-th, 7-th, and 11-th harmonics were included in the system.  Table IX summarizes the results of the simulations.  Figs. 11 and 12 show the improvements before and after three filters suppressing the 5-th, 7-th, and 11-th order harmonic distortions.

We further look at the situation when four filters suppressing the 5-th, 7-th, 11-th, and 25-th harmonics.  Table X summarizes the results from the simulation.  Figs. 13 and 14 show the improvements before and after three filters suppressing the 5-th, 7-th, 11-th, and 25-th order harmonic distortions.  The results demonstrate the fact that installing more filters in the system does not necessary mean better improvements of harmonic distortions.

VI.	CONCLUSIONS

In conclusions, the proposed power distribution model was successfully implemented as a PC-based computer program.  A user-friendly GUI was also integrated with the analysis module for design engineers.

A small industrial plant was selected to demonstrate the developed power distribution model in limiting harmonics and improving reactive compensation.  Results from the simulations show that the developed computer program can reduce costs and design cycle time for designs real-world industrial power distribution systems.

Table IX

SOLUTIONS COMPUTED BY THE PROGRAM

| FILTER | F(#5) | F(#7) | F(#11) |
| --- | --- | --- | --- |
| ni | 4.60 | 6.44 | 10.12 |
| QFi (KVAR) | 2099 | 343 | 433 |
| C (uf) | 487 | 82 | 106 |
| L (mh) | 0.684 | 2.071 | .649 |
| Solution Time: 6.2 Seconds |  |  |  |

THDi=12.618%

THDi=3.232%

Fig. 11. Comparison of harmonic currents before and after the three filters suppressing the 5-th, 7-th, and 11-th harmonics being installed.

THDv=1.273%

THDv=0.446%

Fig. 12. Comparison of harmonic voltages before and after the three filters suppressing the 5-th, 7-th, and 11-th harmonics being installed.

Table X

SOLUTIONS COMPUTED BY THE PROGRAM

| FILTER | F(#5) | F(#7) | F(#11) | F(#25) |
| --- | --- | --- | --- | --- |
| ni | 4.60 | 6.44 | 10.12 | 23 |
| QFi (KVAR) | 1453 | 158 | 1198 | 66 |
| C (uf) | 337 | 37.5 | 289 | 16 |
| L (mh) | 0.986 | 4.524 | .0.238 | .829 |
| Solution Time: 3 minutes and 5.3 Seconds |  |  |  |  |

THDi=12.618%

THDi=5.198%

Fig. 13. Comparison of harmonic currents before and after the four filters suppressing the 5-th, 7-th, 11-th, and 25-th harmonics being installed.

THDv=1.273%

THDv=0.527%

Fig. 14. Comparison of harmonic voltages before and after the four filters suppressing the 5-th, 7-th, 11-th, and 25-th harmonics being installed.

Kun-Ping Lin   was  born  in Taiwan and  received  his B.S.E.E degree from the University of Chung-Yuan, Chung Li, Taiwan, R.O.C, in 1989 and the M.S. degree in electric engineering from National Taiwan University, Taipei, Taiwan, R.O.C, in 1995.

From 1989 to 1993, he was working at the Ming Hoon Electrical Design & Consulting Corporation and his works including, grounding, lighting, cable tray, substation and distribution ,designed for 161kv, 34kv and 11.4kv power system. Most of his work were centered on troubleshooting, flicker, harmonic analysis, motor starting,  relay setting, and filter design. Ever since 1995, he has been a senior  engineer at the Pacific Engineers & Constructors Ltd, invested by Bechtel  Engineers & Constructors  Co. , in U.S.A,  in Taipei. In 1997, he joined Formosa Petrochemical Corporation at Mai Liao in Taiwan and was responsible for a project of co-generation area substation. In 1998, he has retuned to  Ming Hoon Electrical Design & Consulting Company and assumes  a chief  at the power department. At present, he also founded a team to research and improve the harmonic problem generated from the 12 inch semiconductor factory, steel works, arc furnace factory and paper factory.

REFERENCES

[1]	Damian A. Gonzalez and John C. McCall, “Design of filters to reduce harmonic distortion in industrial power systems”, IEEE Trans. on Industrial Applications, vol. IA-23, no. 3, May/June, pp. 504-511, 1987.

[2]	Jose R. Ramos, Alberto Marani, Anfrea cavallini, and Loggini, “A simplified harmonic simulation procedure”, IEEE Industrial Applications Meeting, vol. 2, pp. 1594-1600, 1993.

[3]	Anthony V. Fiacco, “Nonlinear Programming: Sequential Unconstrained Minimization Technique,” George Washington university, 1993.

[4]	Christopher K. Duffey, and Ray P. Stratford, “Update of harmonic standard IEEE-519: IEEE recommended practices and requirements for harmonic control in electrical power systems”, IEEE Trans. on Industrial Applications, vol. 25, no. 6, Nov./Dec., pp. 1025-1034, 1989.

[5]	G. Lemieux, “Power system harmonic resonance - a documented case”, IEEE Trans. vol. IA-26, no.3, May/June, 1990.

[6]	Frederick S. Hillier, “Introduction to operation research”, Stanford University, 1990.